## ABSTRACT
| SEMAC CONSULTANTS PVT LTD, | CLIENT : M/s MEGA FOOD PARK PVT LTD
| ENGINERING DESIGN CONSULTANTS | Project : PROPOSED FOOD PARK DEVELOPMENT AT WAHEGAON VILLAGE , PAITHAN TALUKA , AURANGABAD
| ELECTRICAL DEPARTMENT - HYDERABAD - TELANGANA STATE [India] | Subject : ELECTRICAL DISTRIBUTION WORKS ABSTRACT FOR THE PROPOSED MEGA FOOD PARK PVT LTD
| ISO 9001 : 2008 Certified Company | REV NO : R2 ; Date : 24.09.15 ; Job No : H-13-14/021 ; Doc No - 401
|  |  | SUPPLY |  | ERECTION
SL.No | DESCRIPTION OF WORK | UNIT | Net Supply RATE | Net Supply AMOUNT | Net Erection RATE | Net Erection AMOUNT
| Percentage of taxes and Duties => |  | Rs. | Rs. | Rs. | Rs.
A | Core and infrastructure works [ This Part consists of Core Area 's transformer , HT cable ,HT breakers ,LBS , transformer Earthing , cable trench etc. only , Down the line from the transformer secondary side distribution will be covered in PHASE -2 internal electrical scope ]
B | 11 KV OHL [ this part consists of entire roads with 11 KV OHL works with PSCC poles ] from this OHL to individual leasable plots tapping will be in vendors scope , However for the client scope of building SS,ADMIN,F&V,WH,MSME shead required DP str,HT cable etc covered.
C | INTERNAL ROAD LIGHTING WORKS [ this cost inclusive of octagonal GI poles , LED street light , Earthing , LT Cable for street light , excavation of trench , street light control panel , GATE LIGHT ]
D | 11 KV LIASIONING WORKS [ this cost is Only for Phase -1 works CEIG chief electrical inspector approval , Load sanction works considered , all other deposits and fee will be at actual to be paid by client in line with MHSEB ]
E | LAN & TP WORKS [ this cost is Only for optic fiber for LAN and copper cable for Tele phone considered for external work to cater the site , but the individual leasable plots cables are not considered same will be in respective Vendor scope ]
F | SOLAR STREET LIGHTING WORKS [ This part consist of Hybrid solar street light of 60 watts with octagonal GI poles ]
G | DG SET WORKS [ this part consist of 100% DG back up to ADMIN ,STP /ETP ,Pack house ,Substation ,Road lighting ,Ware House only . From SYN panel to Down the line Distribution like feeder ,cable etc will be in Phase-2 Internal works ]
| TOTAL COST |  | Rs.
| GRAND TOTAL COST |  | Rs.
1 | Important NOTES
1.01 | Contractor shall get prior approval from Owner/ Consultant for quantities of items to be supplied at site. This is to ensure adequate and actual quantities for execution.
1.02 | Contractor shall get approval from the Owner/ Consultant for all Makes of items & its specifications before supply the same at site.
1.03 | All materials used shall be of IS approved and ISI marked. In addition, BEE labeled items shall also be offered.
1.04 | The work shall be carried out strictly as per Electrical Inspectorate & EB standards and only after getting Electrical scheme approval from the Electrical Inspectorate only the execution work starts
1.05 | Item wise tentative quantities are given here. Quantities are subject to change as per site conditions and clients /consultants requirements during Execution . Payment will be made for the actually executed and actually measured quantities at site at agreed rates. No claim for escalation of rates due to increase or decrease in quantities will be considered later.
1.06 | The contractor shall do necessary arrangements to measure Soil Resistivity at the site by the Inspectorate, and shall submit the report to the Owner/Consultant.
1.07 | Preparation of drawings, documents, liaison work, etc. for getting initial/final NOC from EB/ Pollution Control Board/ Electrical Inspectorate and other statutory agencies is also included in the scope of this contract. Contractor shall pay all the statutory fees initially, however, the same will be reimbursed on submission of Original supporting documents.
2 | Note : the following works are not in electrical scope ,
2.01 | TRANSFORMER - FOUNDATION WORK
2.02 | DG - FOUNDATION WORK
2.03 | MASONARY CABLE TRENCH if any
2.04 | LT / HT , RMU ,Feeder pillar PANEL's FOUNDATIONS
2.05 | sub station building construction works
2.06 | Development charge ,security deposit , service charge ,load sanctioning fee , deposits ,supervision charges ,HT meter deposits , scrutiny fees ,HT meter deposits , scrutiny fees , Right of way and land acquisition , Survey etc………………..................................... Not considered.
2.07 | if any National highway clearance approval and road cutting works not considered
| SIGNATURE OF CLIENTS WITH SEAL |  |  |  | SIGNATURE OF BIDDER WITH SEAL

## CORE INFRA
| SEMAC CONSULTANTS PVT LTD, | CLIENT : M/s MEGA FOOD PARK PVT LTD
| ENGINERING DESIGN CONSULTANTS | Project : PROPOSED FOOD PARK DEVELOPMENT AT WAHEGAON VILLAGE , PAITHAN TALUKA , AURANGABAD
| ELECTRICAL DEPARTMENT - HYDERABAD - TELANGANA STATE [India] | Subject : TENDER BOQ FOR CORE AND INFRSTRUCTURE ELECTRICAL DISTIBUTION WORKS FOR THE PROPOSED MEGA FOOD PARK PVT LTD
| ISO 9001 : 2008 Certified Company | Date : 24.09.15 ; Job No : H-13-14/021 ; Doc No - 401 ; REV NO : R2 ;
|  |  |  | SUPPLY | [6 empty] | ERECTION
SL.No | DESCRIPTION OF WORK | UNIT | QTY | BASIC RATE | ED | CST | VAT |  | Net Supply RATE | Net Supply AMOUNT | BASIC RATE | SER. TAX | Net Erection RATE | Net Erection AMOUNT
| Percentage of taxes and Duties => | [10 empty] | 12.36%
PART- A : [ CORE & INFRA STRUCTURE AREA ELECTRICAL WORKS ]
1 | TRANSFORMER (OUT DOOR) :
Supply, loading ,unloading ,store, , erection, testing & commissioning of 11KV/433V, Dyn11, Oil cooled ONAN type Out door mounting type Copper wound continuous duty Transformer with Marshalling Box, Oil Temperature Indicator, Winding Temperature Indicator, Bucholz Relay, Magnetic oil level gauge with alarm, Bidirectional rollers, cable boxes on both side, Pressure Relief Valve, NCT for REFR relay etc., including the first filling of transformer oil and all other accessories as required. The tap off on the side shall be + 10 % / - 10% in steps of 1.25 %. the percentage of impedance etc refer the specification and Drgs. (shall be conforming to IS 11171& IS 2026/IEC 726)
[ Make : Crompton Greaves / Volt Amps / EMCO / BHARAT BIJLEE / ABB ]
1.01 | 100 KVA 11KV/433V, Dyn11, Oil cooled ONAN type Out door continuous duty Transformer with OFF LOAD Transformer [FOR SS & STREET LIGHTING ] | No | 1
1.02 | 250 KVA 11KV/433V, Dyn11, Oil cooled ONAN type Out door continuous duty Transformer with OFF LOAD Transformer [FOR MSME WARE HOUSE & STP ETP ] | No | 2
0
1.03 | 500 KVA 11KV/433V, Dyn11, Oil cooled ONAN type Out door continuous duty Transformer with OFF LOAD Transformer [ FOR ADMIN,LAB,CANTEEN, SECURITY ,WB,DRR ] | No | 1
0
1.04 | 750 KVA 11KV/433V, Dyn11, Oil cooled ONAN type Out door continuous duty Transformer with OFF LOAD Transformer | No | QRO
0
1.05 | 1000 KVA 11KV/433V, Dyn11, Oil cooled ONAN type Out door continuous duty Transformer with OFF LOAD Transformer | No | QRO
0
1.06 | 1250 KVA 11KV/433V, Dyn11, Oil cooled ONAN type Out door continuous duty Transformer with OFF LOAD Transformer | No | QRO
0
1.07 | 1600 KVA 11KV/433V, Dyn11, Oil cooled ONAN type Out door continuous duty Transformer with OFF LOAD Transformer | No | QRO
0
1.08 | 2000 KVA 11KV/433V, Dyn11, Oil cooled ONAN type Out door continuous duty Transformer with OFF LOAD Transformer | No | QRO
0
1.09 | 2500 KVA 11KV/433V, Dyn11, Oil cooled ONAN type Out door continuous duty ON Load Transformer with On LOAD Transformer [ FOR F &V PACK HOUSE] | No | 1
2 | H.T. 11 KV ( E) XLPE Alluminium Armoured Cable :
Supply, laying, testing and commissioning of following size 3-core Earthed HT XLPE insulated Aluminum armoured conductor under ground cable, shall be laid in built up cable trench / already laid RCC Hume pipe / on cable tray / in Excavated ground at a depth As Specified below From Natural / Finished ground level . The cable shall conform to IS 7098/ Part II and as on date latest revision in IS standards
Note: Excavation and refilling of any type of earth soil, with supply and providing cable protection by half cut heavy duty Hume pipe with 150 mm river sand bed and top including C.I cable route marker will be operated under schedule heading of "Civil Works for outdoor cable laying".
[ MAKES : Universal / CCI-Tropodur / KEI / RPG / RR )
2.01 | 3-Core x 185 Sqmm 11 KV (E) XLPE Aluminum Armoured Cable | Rmt | 300
0
2.02 | 3-Core x 300 Sqmm 11 KV (E) XLPE Aluminum Armoured Cable | Rmt | 200
3 | H.T. Cable End Termination : |  | 0
| Supply , providing ,testing and commissioning of 11KV (E) HT cable termination kit for indoor/ outdoor Heat shrinkable end termination kit suitable for the HT XLPE cable with all sundry material like BI-metallic Lugs using crimping , including Earthing of termination kit etc. full set complete. |  | 0
[ MAKE: RAYCHEM ]
3.01 | 3-Core x 185 Sqmm 11 KV (E) XLPE Aluminum Armoured Indoor End Termination : | No | 4
3.02 | 3-Core x 185 Sqmm 11 KV (E) XLPE Aluminum Armoured Out door End Termination : | No | 4
0
3.03 | 3-Core x 185 Sqmm 11 KV (E) XLPE Aluminum Armoured STRAIGHT THROUGH JOINT kit full set complete as required | No | 1
0.01 | 3-Core x 300 Sqmm 11 KV (E) XLPE Aluminum Armoured Indoor End Termination : | No | 4
0.02 | 3-Core x 300 Sqmm 11 KV (E) XLPE Aluminum Armoured Out door End Termination : | No | 4
0
0.03 | 3-Core x 300 Sqmm 11 KV (E) XLPE Aluminum Armoured STRAIGHT THROUGH JOINT kit full set complete as required | No | 1
4 | Heavy Duty Hume pipe. [NP4 ] |  | 0
4 | Supply and laying of following dia RCC Heavy Duty Hume pipes with all accessories like collars and bends and nipples as required for road crossings, laid below ground level at minimum depth of 1000mm or under paved areas/under floor with including all civil engineering works as required.
(sample to be get approved From client/consultant )
4.01 | 300 mm dia NP4 Hume pipe. | Rmt | 140
0
4.02 | 450 mm dia NP4 Hume pipe. | Rmt | 1200
0
4.03 | 600 mm dia NP4 Hume pipe. | Rmt | 100
0
5 | CIVIL WORKS FOR OUTDOOR CABLE LAYING : |  | 0
| supply , Excavation of outdoor cable trenches at a depth specified below From Ground Level with including excavation at any type of soil as per site condition requirements and providing sand layer bed cushioning for cable, providing HALF CUT HEAVY DUTY HUME PIPE for entire length covering and refilling the trench and making good surface as required. quoted cost inclusive of Providing HT / LT cable route marker at every 15 Mtrs distance. |  | 0
5.01 | Trench of width 600mm & depth 1000mm. | Rmt | 50
0
5.02 | Trench of width 450mm & depth 1000mm. | Rmt | 150
0
5.03 | Trench of width 300mm & depth 1000mm. | Rmt | 150
0
7 | EARTHING - CPRI APPROVED |  | 0
0
7.01 | SUPPLY & Providing C.I PIPE Earth station, with 100 mm internal dia 13mm thick C.I pipe 3 mtr long CI pipe with 2 runs of 50 x 6 mm Hot Dip Galvanized GI strips of each 3 Meter long with including Excavation of earth pit in any type of soil and construction of 230mm thick brick trough (450 mm length x 450mm wide x 450 inner trough clearance ), providing meshed funnel, CI heavy duty ISI approved Square type cover , C.I heavy duty rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper /bimetallic/ GI bolt nut washer etc, completely as per IS 3043, 1987 or latest revision.[ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | 16
7.02 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 3 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 100 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | 2
0
7.03 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 3 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 250 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | 4
7.04 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 6 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 500 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | 2
0
7.05 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 40 x 6 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 750 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | QRO
7.06 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 50 x 6 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 1000 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | QRO
0
7.07 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 60 x 6 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 1250 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | QRO
7.08 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 80 x 6 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 1600 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | QRO
0
7.09 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 60 x 10 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 2000 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | QRO
7.1 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 75x 10 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 2500 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | 2
7.11 | Supply and Providing Substation earth-mat Design, engineering, supply inclusive of corrosion protection measures if any,laying of earth-mat conductors of Hot dip galvanized flats of size 75X10 mm to the approval of Project Manager, excavation, welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc of ground conductors along with risers (of size 50X6 mm GI flats) etc back filling and good compaction,grounding driven rods(40 mm MS solid rod),perforated GI pipes for treated earth pits(with details of treatment as per IS). The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 750mm from the finished ground level.For provision of treated earth-pit and untreated earth pit, refer the specification for designing. Provision of water taps inside the switch yard areas and peripheral treated and un-treated earth pit are required to be provided for watering the treated earth pits. The no. of treated and un treated earth pits are to be done as per the practice and as indicated in the drawing for different equipments. This is as per approved drawing and specification. spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision.
a | 75 x 10 mm Hot Dip Galvanized GI strip | Rmt | 1500
b | 50 x 6 mm Hot Dip Galvanized GI strip | Rmt | 500
c | 25 x 6 mm Hot Dip Galvanized GI strip | Rmt | 350
d | 50MM GI PIPE FOR TREATED EARTH PIT ELECTRORDE WITH CHAMBER AND COVER | Rmt | 100
8 | EAR THING TAPES / WIRES: [ ETP Grade material (as per IS:191 ] |  | 0
0
| Supply and installation of following size Copper / Hot Dip Galvanized GI strip including all fixing accessories for laid inside the building with all necessary interconnections with earth station and equipments with end terminated with suitable copper lugs ,copper fixing or bimetallic hardware's. Below ground joints should be welded / Brazed only. the cost shall include excavation, backfilling, compaction, construction of chambers with all civil works as required. |  | 0
8.01 | 25x 3 mm Copper Tape ( for 100 KVA Neutral ear thing ) | Rmt | 60
8.02 | 25x 3 mm Copper Tape ( for 250 KVA Neutral ear thing ) | Rmt | 100
8.03 | 25x 6 mm Copper Tape ( for 500 KVA Neutral ear thing ) | Rmt | 60
8.04 | 40x 6 mm Copper Tape ( for 750KVA Neutral ear thing ) | Rmt | QRO
8.05 | 50x 6 mm Copper Tape ( for 1000 KVA Neutral ear thing ) | Rmt | QRO
8.06 | 60 x 6 mm Copper Tape ( for 1250 KVA Neutral ear thing ) | Rmt | QRO
8.07 | 80 x 6 mm Copper Tape ( for 1600KVA Neutral ear thing ) | Rmt | QRO
8.08 | 60 x10 mm Copper Tape ( for 2000 KVA Neutral ear thing ) | Rmt | QRO
8.09 | 75 x10 mm Copper Tape ( for 2500 KVA Neutral ear thing ) | Rmt | 100
8.1 | 25 x 6 mm Hot Dip Galvanized GI strip ( for Body earthing ) | Rmt | 250
8.11 | 50 x 6 mm Hot Dip Galvanized GI strip (for Body earthing ) | Rmt | 300
0
9 | STEEL ITEMS |  | 0
0
| Supply, fabrication, erection painting of all type of steel items (ISMC,ISMB,ISA,etc.., as required as per specification complete. Generally steel items For cable trays, BT's supporting arrangements, checkers plates above trenches and any other steel items not covered in other items of schedule of quantities. The quoted rate should inclusive of painting the steel items with two coats of red oxide primer and two coats of synthetic enamel paint of approved shade. | MT | 2
[ Make:- Jindal / TATA / Vizag ]
17 | Compact out door type LBS + Earth switch With Metering cuble HT trivector meter
[ Makes: Siemens/ ABB/ Schneider / CG ]
17.01 | Supply, installation, testing and commissioning of 11 KV indoor Compact type 1Nos. 630A Isolators +Fuse units with EARTH SWITCH as a incomers , Rated STR: 21kA/ 1 Sec & Rated Bus bar Current - 630A has a completely sealed system with a stainless steel tank containing all the live parts and switching functions. A sealed steel tank with constant atmospheric conditions ensures a high level of reliability as well as personnel safety and a virtually maintenance-free system Ring Main Unit (Both sides extensible) outdoor type with transformer control and protection IP 54 Degree of protection The switching station where the RMU is proposed shall have Auxiliary AC supply ,,Interlocked Medium Voltage cable test access (no need to remove cable terminations or use loose earthing devices) Integral self-powered protection with TFL, adjustable curve , SELF POWERED RELAYS ,Earth screened cast-resin gas module Range of dry type metering units ,Mechanical tripped on-fault indication ,Simple to follow mimic providing user-friendly operation ,Resin encapsulated bus bars in air bus chamber for extensible version with cable connection chamber cost inclusive of Supply and fixing of HT Trivector Meter CTs of 0.5 Class accuracy with TOD function in meter as per standards and specifications . | No | 4
COMPACT out door type SF6 /VCB With Metering cuble HT trivector meter
17.02 | Supply, installation, testing and commissioning of 11 KV out door Compact VCB , consisting of 1Nos cable chamber and 1Nos. 630/800 A Vacuum Circuit Breaker with O/C + E/F ,transformer protections relay Rated STR: 21kA/ 1 Sec & Rated Bus bar Current - 630A , The RMU has a completely sealed system with a stainless steel tank containing all the live parts and switching functions. A sealed steel tank with constant atmospheric conditions ensures a high level of reliability as well as personnel safety and a virtually maintenance-free system Ring Main Unit (Both sides extensible) outdoor type .with transformer control and protection IP 54 Degree of protection for SF6 chamber-IP 67 Degree of protection. The switching station where the RMU is proposed shall have Auxiliary AC supply . Gas pressure indicator as standard ,Anti-reflex operating handle with facilities for electrical operation ,Interlocked Medium Voltage cable test access (no need to remove cable terminations or use loose earthing devices) Integral self-powered protection with TFL, adjustable curve , SELF POWERED RELAYS ,Earth screened cast-resin gas module Range of dry type metering units ,Mechanical tripped on-fault indication ,Simple to follow mimic providing user-friendly operation ,Resin encapsulated bus bars in air bus chamber for extensible version cost inclusive of Supply and fixing of HT Trivector Meter 100/5 with 4 CTs of 0.5 Class accuracy with TOD function in meter as per standards and specifications | No | QRO
17.03 | 11KV - 1 Module HT VCB Indoor expandable type
Supply, Installation, Testing and Commissioning of 11KV, 1 No 800 A VCB [ 26 KA / 3 sec ] The VCB Panel horizontal withdrawals made of 14 Swg CRCA Sheet Steel Clad, Synthetic Epoxy powder coated finish painted, totally enclosed free standing cubicle type , suitable for operation on 11KV 3Ph, 50Hz, AC earthed system. full set complete with bus bar inter connections control wiring designation labels, caution notices, sealing and pad locking facilities wherever necessary space provision for entry of HT cables from the bottom through detachable gland plates. with relay and metering two cubic compartments, 230V AC Spring charging Motor mechanism, trip circuit shall be operated on 110V DC and as per the detailed specifications. Separate CT's are to be provided for Protection and Metering of burden 50VA ,15KV class of 0.5 accuracy for metering and protection as 5 P 10 with the panel shall consist of suitable rating TPN +E Electrolyte Al bus bar (at the rating of 0.8A Sq.mm) supported with DMC/ SMC barriers and color coded with Heat shrinkable sleeves.
Incomer module shall be with 11000v /√3 / 110V /√3 CL. 0.2/50VA, Potential Transformers, panels shall be of Bottom Cable Entry only. Panels shall be extendable type on either ends. Every VCB shall be provided with ON/OFF /Trip Indication lamps of LED type. 8 Window Annunciation panel with windows of 1) O/C Tripped, 2) E/F Tripped, 3) DC Supply Fail 5) winding temp, 6) bucholz alarm 7 ) oil temp 8) spares ., Spring Charge and Trip Circuit Healthy indications with Local / Remote switch. The rate shall inclusive of All fixing hardware's ,self powered DC operated relay and self power back as required.
| [ MAKE: SIEMENS /ABB /SCHINIDER / /MEI /CROMPTON GREAVES ] | No | 1
TOTAL COST
GRAND TOTAL OF SUPPLY AND ERECTIONS ====>
| TOTAL VALUE OF E.D |  | 0
0
| TOTAL VALUE OF CST |  | 0
0
| TOTAL VALUE OF VAT |  | 0
0
| TOTAL VALUE OF SER. TAX |  | 0
0
| GRAND TOTAL INCLUSIVE OF ALL DUTIES & TAXES |  | 0
0
Note :
Quoted cost should inclusive of all taxes , duty ,octroi, transport etc
internal works not considered
EXCLUSION
TRANSFORMER - FOUNDATION WORK
DG - FOUNDATION WORK
MASONARY CABLE TRENCH WORK
LT /HT PANEL - FOUNDATION WORK
internal distribution and internal work panel ,cables ,lighting etc not considered.
| SIGNATURE OF CLIENTS WITH SEAL | [6 empty] | SIGNATURE OF BIDDER WITH SEAL

## 11- OHL
| SEMAC CONSULTANTS PVT LTD, | CLIENT : M/s MEGA FOOD PARK PVT LTD
| ENGINERING DESIGN CONSULTANTS | Project : PROPOSED FOOD PARK DEVELOPMENT AT WAHEGAON VILLAGE , PAITHAN TALUKA , AURANGABAD
| ELECTRICAL DEPARTMENT - HYDERABAD - TELANGANA STATE [India] | Subject : TENDER BOQ FOR EXTERNAL 11KV OHL WORKS FOR THE PROPOSED MEGA FOOD PARK PVT LTD
| ISO 9001 : 2008 Certified Company | Date : 24.09.15 ; Job No : H-13-14/021 ; Doc No - 401 REV NO : R2 ;
|  |  |  | SUPPLY | [6 empty] | ERECTION
SL.No | DESCRIPTION OF WORK | UNIT | QTY | BASIC RATE | ED | CST | VAT |  | Net Supply RATE | Net Supply AMOUNT | BASIC RATE | SER. TAX | Net Erection RATE | Net Erection AMOUNT
| Percentage of taxes and Duties => | [10 empty] | 12.36%
PART- B : 11 KV OHL WORKS
1 | 11 KV POINT OF SUPPLY & METERING YARD - [STEEL Make:- Jindal / TATA / Vizag ]
1.01 | Supply, Erection testing and commissioning of DP Structure consist of 2 Nos of 100 x 75 mm ISMB Steel Poles 11 Mtrs long pole , 9.0 Meter long above at ground level and 2.0 meters long below the ground by digging a pit of 2 meters depth and Refilling back with 1:2:4 PCC/RCC Foundation with cross arms, pin and disc insulators, 800A AB switch Double break with GI Guide line with operating handle with lockable arrangement , DO fuse, Lightning Arrestor, earthing of LA and body parts including MS items as per specifications and standards of MHSEB and . Supply and fixing of LT Trivector Meter 500/5 in P.P Box with 4 CTs of 0.5 Class as per standards and specifications of MHSEB complete from MHSEB approved vendors. Supply and installation of Rural Type Distribution board as per standards and specifications of MHSEB complete . Labour charges for connection of metering board and provision of HT supply including all labour complete Civil RCC Foundation with coping, and two Cots of Painting over a cote of Zinc corrosive red oxide. Complete body earthing by 1R-25x6 mm GI strip with DMC insulator all other associate work required by state Electricity Board. (All Steel Material Make :- Jindal / Vizag / Tata ). refer the tender drawing further [ MHSEB PORTION ] | SET | QRO
1.02 | Supply, Erection testing and commissioning of DP Structure consist of 2 Nos of 100 x 75 mm ISMB Steel Poles 11 Mtrs long pole , 9.0 Meter long above at ground level and 2.0 meters long below the ground by digging a pit of 2 meters depth and Refilling back with 1:2:4 PCC/RCC Foundation with cross arms, pin and disc insulators, 800A AB switch Double break with GI Guide line with operating handle with lockable arrangement , DO fuse, Lightning Arrestor, earthing of LA and body parts including MS items as per specifications and standards of MHSEB , supply including all labour complete Civil RCC Foundation with coping, and two Cots of Painting over a cote of Zinc corrosive red oxide. Complete body earthing by 1R-25x6 mm GI strip with DMC insulator all other associate work required by state Electricity Board. (All Steel Material Make :- Jindal / Vizag / Tata ). refer the tender drawing further [ Client's PORTION ] | SET | 7
2 | YARD FENCING & JELLY SPREADING
[STEEL Make:- Jindal / TATA / Vizag ]
2.01 | supply and Providing 2500 mm high chain link fencing consisting of 50 x 50 x 6 mm ISA angle, vertical support port 2500 mm high (spacing not exceeding 2.5m), 50 x 50 x6 mm ISA angle 3000 mm long bracing struts (in both directions) for every fifth post (and at change of directions of the fence) and 10 gauge GI chain link mesh 50 x 50 mm fully stretched and secured to ISA angle verticals and horizontals with 6mm dia GI bolts, nuts and washers spaced at 150 mm (min) using 25 x6 mm GI flat cover strips, 170 mm long, bottom 75mm end of MS verticals and bracing struts to be split and 400 mm embedded in 400 x 400 x 500 deep cement concrete 1:3:6 including necessary welding and/or bolted connections of MS horizontals and bracings/struts to vertical posts, excavation, cement concrete and painting one coat of primer and two coats of synthetic enamel paint to all exposed faces of steel work and chain link fencing. Measured net area of fencing between external faces of horizontal members. The quoted cost inclusive of bottom brick retaining wall for the entire length as required [ pls refer the civil drawings ] | Rmt | 35
2.02 | Supply and providing Steel gate 2.4 mm wide (min) in two (side hung) leaves to match the chain link fence including necessary hinges, Steel work welded, frame-works M.S. round or square bars in fencing grills including cutting, hoisting, fixing and applying two coat priming and one coat grey paint locking arrangements, etc.,complete.as per drawings. | MT | 0.5
2.03 | Supplying and spreading 40mm nominal size black granite jelly 150mm depth and over the 50mm River sand filling as directed the work etc. | Cum | 30
3 | MISCELLANEOUS WORKS :
3.01 | Supplying & Erection of 11 kV danger boards, as per STATE ELECTRICITY BOARD requirement. | No | 3
3.02 | Supplying & Erection of Rubber mats of 11 KV grade 2.0 Mtrs x 1.0 Mtrs and of sufficient 12mm thickness as required by the Electrical Inspectorate and confirming to IS 5424. | No | 1
3.03 | Supply and Installation of 5KG capacity ABC type fire extinguishers complete with mounting brackets, spray nozzles, connecting pipes, "OPEN / CLOSE" valves with all other necessary accessories complete as required. (make: USHA, Firepro/Agnice/UTC, Ceasefire ). | No | 1
3.04 | supply and providing of 11KV grade hand gloves with chalk powder including suitable weather proof transparent box with lock and key | set | 1
3.05 | Supply and providing of First Aid Box as per IS standard. | No | 1
3.06 | Supply and providing 4 nos of red color painted Fire buckets round bottom of 9 Liters capacity filled with dry sand with including suitable angle iron support red color painted. | No | 1
3.07 | Supply and Fixing of shock treatment Chart ( English & local state language ) as per CEIG /CEA standard with laminated frame. | No | 1
4 | 11KV (E) HT XLPE H.T Cable :
Supply, laying, testing and commissioning of following size 3-core-11KV (E) HT XLPE insulated Aluminum Armoured under ground cable, shall be laid in builted up cable trench / already laid RCC Heavy Duty Hume pipe / on cable tray / in buried ground at a depth of 1000mm below ground level . The cable shall conform to IS 7098- Part II.
Note: Excavation and refilling of any type of Soil earth, with supply and providing cable protection with sand Bed half cut Heavy Duty Hume pipe ( or ) with sand Bed and bricks on both side cables and top cable with including C.I cable route marker at 15 meter interval will be operated under schedule heading of "Civil Works for outdoor cable laying".
[ MAKES : Universal / CCI-Tropodur / KEI / RPG / RR )
4.01 | 3-Core x 300 Sqmm 11KV (E) XLPE Aluminum Armoured Cable - | Rmt | 200
5 | 11KV (E) H.T. Cable End Termination :
Supply , providing ,testing and commissioning of 11KV (E) HT cable termination kit for indoor/ outdoor Heat shrinkable end termination kit suitable for the HT XLPE cable with all sundry material like BI-metallic Lugs using crimping , including Earthing of termination kit etc. full set complete.
[ MAKE: RAYCHEM ]
5.01 | 3-Core x 300 Sqmm 11 KV (E) XLPE Aluminum Armoured Indoor End Termination : | No | 2
5.02 | 3-Core x 300 Sqmm 11 KV (E) XLPE Aluminum Armoured Out door End Termination : | No | 2
5.03 | 3-Core x 300 Sqmm straight through joints Termination : | No | 1
6 | EARTHING - CPRI APPROVED
6.01 | SUPPLY & Providing C.I PIPE Earth station, with 100 mm internal dia 13mm thick C.I pipe 3 mtr long CI pipe with 2 runs of 50 x 6 mm Hot Dip Galvanized GI strips of each 3 Meter long with including Excavation of earth pit in any type of soil and construction of 230mm thick brick trough (450 mm length x 450mm wide x 450 inner trough clearance ), providing meshed funnel, CI heavy duty ISI approved Square type cover , C.I heavy duty rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper /bimetallic/ GI bolt nut washer etc, completely as per IS 3043, 1987 or latest revision. [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | 4
6.02 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 3 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 100 KVA Transformer Neutral earthing ) [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | 4
7 | EAR THING TAPES / WIRES: [ ETP Grade material (as per IS:191 ]
Supply and laying of following size Earth strip with fixing GI /Copper accessories , necessary interconnections between earth station and equipments, incase of copper bare wire the end to be terminated with suitable copper lugs ,copper fixing hardware's. the quoted cost should inclusive of civil excavation and refilling works where ever required. the earth strip under ground joints must be welded / copper Brazed only.
7.01 | Hot dip galvanized 50 x 6 mm GI tape with GI fixing hardware's. | Rmt | 50
7.02 | Hot dip galvanized 25 x 6 mm GI tape with GI fixing hardware's. | Rmt | 75
7.03 | 8 SWG Copper wire ETP Grade material (as per IS:191) with copper fixing hardware's. | Rmt | 60
7.04 | 25 x 3 mm copper tape ETP Grade material (as per IS:191) with copper fixing hardware's. | Rmt | 50
8 | 11KV - 1 Module HT VCB Indoor expandable type
Supply, Installation, Testing and Commissioning of 11KV, 1 No 800 A VCB [ 26 KA / 3 sec ] The VCB Panel horizontal withdrawals made of 14 Swg CRCA Sheet Steel Clad, Synthetic Epoxy powder coated finish painted, totally enclosed free standing cubicle type , suitable for operation on 11KV 3Ph, 50Hz, AC earthed system. full set complete with bus bar inter connections control wiring designation labels, caution notices, sealing and pad locking facilities wherever necessary space provision for entry of HT cables from the bottom through detachable gland plates. with relay and metering two cubic compartments, 230V AC Spring charging Motor mechanism, trip circuit shall be operated on 110V DC and as per the detailed specifications. Separate CT's are to be provided for Protection and Metering of burden 50VA ,15KV class of 0.5 accuracy for metering and protection as 5 P 10 with the panel shall consist of suitable rating TPN +E Electrolyte Al bus bar (at the rating of 0.8A Sq.mm) supported with DMC/ SMC barriers and color coded with Heat shrinkable sleeves.
| Incomer module shall be with 11000v /√3 / 110V /√3 CL. 0.2/50VA, Potential Transformers, panels shall be of Bottom Cable Entry only. Panels shall be extendable type on either ends. Every VCB shall be provided with ON/OFF /Trip Indication lamps of LED type. 8 Window Annunciation panel with windows of 1) O/C Tripped, 2) E/F Tripped, 3) DC Supply Fail 5) winding temp, 6) bucholz alarm 7 ) oil temp 8) spares ., Spring Charge and Trip Circuit Healthy indications with Local / Remote switch. The rate shall inclusive of All fixing hardware's ,self powered DC operated relay and self power back as required. | No | QRO
[ MAKE: SIEMENS /ABB /SCHINIDER / /MEI /CROMPTON GREAVES ]
9 | Over Head Line POLE PIT
9.01 | Excavation of pole pit for planting of the poles on the approved route including all civil works associated like excavation, concreting coping etc pit size 0.45 M x 0.45 M x 1.8 M at any type of soil for 11.0 M poles with including dewatering, Shoring and shuttering as necessary and back filling the pit (after erection and concreting ,coping of the poles ) with excavated earth / extra earth / excavated rock bits if any and leveling the site without any lead. ( in wet soil and black cotton soil planting depth of pole may be increased by 0.2 to 0.3 Mtrs and wind span limited). 1:2:4 RCC Foundation aligning. The size of the pit will be having a depth of 1/6 of the full length of the support. | No. | 55
10 | Pole with spiral coil pole earthing @ 40 / 45 MTRS SPAN
10.01 | Supply & Erection ,aligning of PSCC Poles of 11 Mts height and weight not less than 365 Kg for 11KV , 3 phase Dual circuit ( as per REC standards ) with Base Plate , including supply and fixing spiral earth coils, MS "V" cross Arm / Straight cross Arm Channel, top cleat, all type of Insulator with GI Pin , V Cross Arm & Pole Top Bracket (F Clamp) , Disc/strain insulators with metal parts, 75mm padding with concrete, earthing, anti climbing device with fasteners, danger plate, nuts, bolts & washers, insulator bindings cables/ conductors in all respect complete with all GI hardware and earth coils , Dead end clamp / Anchor clamp assembly including brackets, pole clamps, Suspension clamp, the rates quoted shall inclusive of transport of all materials ( but excluding the cost of the pit excavation concreting and back filling ). | No. | 10
10.02 | Supply & Erection ,aligning of PSCC Poles of 11 Mts height and weight not less than 365 Kg for 11KV , 3 phase single circuit ( as per REC standards ) with Base Plate , including supply and fixing spiral earth coils, MS "V" cross Arm / Straight cross Arm Channel, top cleat, all type of Insulator with GI Pin , V Cross Arm & Pole Top Bracket (F Clamp) , Disc/strain insulators with metal parts, 75mm padding with concrete, earthing, anti climbing device with fasteners, danger plate, nuts, bolts & washers, insulator bindings cables/ conductors in all respect complete with all GI hardware and earth coils , Dead end clamp / Anchor clamp assembly including brackets, pole clamps, Suspension clamp, the rates quoted shall inclusive of transport of all materials ( but excluding the cost of the pit excavation concreting and back filling ). | No. | 43
10.03 | same as above item but with 200 x 100 mm ISMB weight 25.4 kg per mtr for Dual circuit | No. | 1
10.04 | same as above item but with 1 00 x 75 mm ISMB weight 25.4 kg per mtr for single circuit | No. | 1
11 | CIRCUIT BREAK / ISOLATION POINT
11.01 | Supply, Erection testing and commissioning of DP Structure consist of 2 Nos of 100 x 75 mm ISMB Poles 11 Mtrs long pole ,9.0 Meter long above at the ground and 2.0 meters long below ground by digging a pit of 2 meters depth Refilling back with 1:2:4 RCC Foundation ,fixing spiral earth coils, steel cross members to support all type of insulators AB switch etc suitable for Dual circuit GI -V- shape cross arm, with 2 no of 11KV 800A ON LOAD AB Switches Double break with GI Guide lines with operating handles with lockable arrangement looping HT aerial bunched cables with necessary angle iron supports complete with hardware (including the cost of the pit excavation, concreting and back filling ,transport of all materials .). inclusive of the supply and erect Dead end clamp / Anchor clamp assembly brackets, pole clamps, Suspension clamp assembly etc. Quoted cost inclusive of 11 KV Aerial bunched cable Jumper, and two Cots of Painting over a cote of Zinc corrosive red oxide. Complete body earthing by 1R-25x6 mm GI strip with DMC insulator all other associate work required by state Electricity Board. Complete body earthing by 1R-25x6 mm GI strip with DMC insulator all other associate work required by state Electricity Board. Channel and angle for supporting 11 KV 2-pole AB Switch, HG Fuse unit, Channel for supporting insulators, anti climbing device with fasteners, danger plate, nuts bolts & washers, preformed insulator binding, and required hardware,, [All Steel Material Make :- Jindal / Vizag / Tata refer the tender drawing further ] | No. | 7
11.02 | Supply, Erection testing and commissioning of FOUR POLE Structure consist of 4 Nos of 100 x 75 mm ISMB Poles 11 Mtrs long pole ,9.0 Meter long above at the ground and 2.0 meters long below ground by digging a pit of 2 meters depth Refilling back with 1:2:4 RCC Foundation ,fixing spiral earth coils, steel cross members to support all type of insulators AB switch etc suitable for Dual circuit GI -V- shape cross arm, with 4 no of 11KV 800A ON LOAD AB Switches Double break with GI Guide lines with operating handles with lockable arrangement looping HT aerial bunched cables with necessary angle iron supports complete with hardware (including the cost of the pit excavation, concreting and back filling ,transport of all materials .). inclusive of the supply and erect Dead end clamp / Anchor clamp assembly brackets, pole clamps, Suspension clamp assembly etc. Quoted cost inclusive of 11 KV Aerial bunched cable Jumper, and two Cots of Painting over a cote of Zinc corrosive red oxide. Complete body earthing by 1R-25x6 mm GI strip with DMC insulator all other associate work required by state Electricity Board. Complete body earthing by 1R-25x6 mm GI strip with DMC insulator all other associate work required . . Channel and angle for supporting 11 KV AB Switch, HG Fuse unit, Channel for supporting insulators, anti climbing device with fasteners, danger plate, nuts bolts & washers, preformed insulator binding, and required hardware, [All Steel Material Make :- Jindal / Vizag / Tata refer the tender drawing further ] | No. | 2
12 | Turn Angle / Cut point with inclusive of spiral coil earthing
12.01 | Supply & Erection ,aligning of 90 Degree angle cut point for 11KV 3 phase Single circuit line , MS "V" / Straight cross Arm Channel, four way /four direction circuit through with necessary jumper ,jumper supports with cross channels and insulators with 4 nos - 11 Mtrs PSCC (each weight not less than 365 KG as per REC ) with Base Plate including pole erection, cross Channel arms, clamps, strain insulators ,pin insulators with pins with metal channel Supports , 4 nos stay sets complete with guy insulator and concreting, G.I. bolts & nuts, spring washers and earth coils. supply of all type insulators & metal parts as required . the rates quoted inclusive of 11KV Lightning arrestor , 11 kv aerial bunched cable Jumper, pin insulators with pins, Disc/strain insulators with metal channels supports And 1:2:4 RCC Foundation aligning, Dead end clamp / Anchor clamp assembly brackets, clamps, Suspension clamp assembly with 4 no of 11KV 800A ON LOAD AB Switch with GI Guide line with operating handle with lockable arrangement etc. refer the tender drawing further , | No. | 1
12.02 | Supply & Erection ,aligning of 90 Degree angle cut point for 11KV 3 phase Dual Circuit line , MS "V" / Straight cross Arm Channel, four way /four direction circuit through with necessary jumper ,jumper supports with cross channels and insulators with 4 nos - 11 Mtrs PSCC (each weight not less than 365 KG as per REC ) with Base Plate including pole erection, cross Channel arms, clamps, strain insulators ,pin insulators with pins with metal channel Supports , 4 nos stay sets complete with guy insulator and concreting, G.I. bolts & nuts, spring washers and earth coils. supply of all type insulators & metal parts as required . the rates quoted inclusive of 11KV Lightning arrestor , 11 kv aerial bunched cable Jumper, pin insulators with pins, Disc/strain insulators with metal channels supports And 1:2:4 RCC Foundation aligning, Dead end clamp / Anchor clamp assembly brackets, clamps, Suspension clamp assembly with 4 no of 11KV 800A ON LOAD AB Switch with GI Guide line with operating handle with lockable arrangement etc. refer the tender drawing further , | No. | 1
12.03 | Supply & Formation of end point (vertical /horizontal) ) cut point for 11KV line with 11 Mtrs PSCC Poles (each weight not less than 365 KG as per REC ) including pole erection, cross arms, clamps, strain insulators with metal parts, pin insulators with pins, 2Nos. stay set complete including guy insulator and concreting, G.I. bolts & nuts, spring washers and earth coils. supply all the insulators & metal parts wherever required in execution of this work and the rates mentioned are including the cost of pin insulators with pins, Disc/strain insulators with metal parts. and 1:2:4 RCC Foundation aligning, Dead end clamp / Anchor clamp assembly brackets, pole clamps, Suspension clamp assembly etc. refer the tender drawing further | No. | 1
12.04 | Supply & Formation of Dead end point for 11KV 3 phase Single circuit line , MS "V" / Straight cross Arm Channel, 11 Mtrs PSCC Poles (each weight not less than 365 KG as per REC ) including pole erection, cross arms, clamps, strain insulators with metal supports ; the rates mentioned are inclusive the cost of 1 Nos stay set complete including guy insulator and concreting, G.I. bolts & nuts, spring washers and earth coils Disc/strain insulators with metal parts and 1:2:4 RCC Foundation aligning, Dead end clamp / Anchor clamp assembly brackets, pole clamps, Suspension clamp assembly etc. | No. | 1
12.05 | Supply & Formation of Dead end point for 11KV 3 phase DUAL circuit line , MS "V" / Straight cross Arm Channel, 11 Mtrs PSCC Poles (each weight not less than 365 KG as per REC ) including pole erection, cross arms, clamps, strain insulators with metal supports ; the rates mentioned are inclusive the cost of 1 Nos stay set complete including guy insulator and concreting, G.I. bolts & nuts, spring washers and earth coils Disc/strain insulators with metal parts and 1:2:4 RCC Foundation aligning, Dead end clamp / Anchor clamp assembly brackets, pole clamps, Suspension clamp assembly etc. | No. | 1
13 | Over Head Line (AAAC) as per Indian Standard 398 Part -IV : 1994 & Up To Date latest amendment [Unit Per RMT is for 3 phase ]
13.01 | Supply, receive, store, stringing /Paving , testing & commissioning of Laying, spreading, lifting, jointing and final sagging of Conductor in accordance with profiles and sag chart including binding, jumpering and fixing of all accessories in 3 nos. conductor in parallel [ R Y B] stringing of three runs of AAA conductor from pole to pole firmly fixed to the pin insulators using binding wires. 11 KV AAAC conductor as Per IS 398 ( part - IV ) and latest standard (suitable current carrying capacity 450 Amps at 65 degree ) Conductor as stringing duly arranging temporary guys, tensioning, sagging of conductor maintaining the ground clearances as per IE rules 1956, pin binding, strain insulator binding and giving jumpers etc, including all transportation ,fixing binding accessories as required. [ 100 SQ MM , 7 x 4.26 mm mm Dia ,ultimate breaking 29 .26 [Kn] 0.3390 Resistance @ 20 Degree C ] Unit Per RMT is for 3 phase . | RMT | 1400
13.02 | Numbering of poles with Letter in white paint and black paint background. | No. | 28
13.03 | Supply, receive, store, stringing /Paving , testing & commissioning of Laying, cradle guarding for road crossings using GI wires and earthing the same) Guarding between two poles like Single/Double/Tri./Four Poles etc. to guard LT/11 KV/Telephone lines, Road/River crossing etc. with G.I. Wire 6 SWG and G.I. Wire 8 SWG including fixing of guarding channel with clamps and nuts and bolts as per relevant drawing. | RMT | 150
14 | Heavy Duty Hume pipe. [NH4 ]
Supply and laying of RCC heavy duty Cement pipes in ground including chipping / excavation laying and making good the surface as required with all accessories like collars and bends and nipples required pipe shall be laid at a depth of 1000 mm below Finished ground level or under paved areas/under floor with including all type of civil engineering works as required. (sample to be get approved From client/consultant )
14.01 | 300 mm dia Hume pipe. | RMT | 50
14.02 | 450 mm dia Hume pipe. | RMT | 50
14.03 | 600mm dia Hume pipe. | RMT | 50
15 | EARTHING - CPRI APPROVED
15.01 | SUPPLY & Providing C.I PIPE Earth station, with 100 mm internal dia 13mm thick C.I pipe 3 mtr long CI pipe with 2 runs of 50 x 6 mm Hot Dip Galvanized GI strips of each 3 Meter long with including Excavation of earth pit in any type of soil and construction of 230mm thick brick trough (450 mm length x 450mm wide x 450 inner trough clearance ), providing meshed funnel, CI heavy duty ISI approved Square type cover , C.I heavy duty rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper /bimetallic/ GI bolt nut washer etc, completely as per IS 3043, 1987 or latest revision. [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No. | 6
15.02 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 3 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No. | 6
15.03 | Supply and Providing Substation earth-mat Design, engineering, supply inclusive of corrosion protection measures if any,laying of earth-mat conductors of Hot dip galvanized flats of size 75X10 mm to the approval of Project Manager, excavation, welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc of ground conductors along with risers (of size 50X6 mm GI flats) etc back filling and good compaction,grounding driven rods(40 mm MS solid rod),perforated GI pipes for treated earth pits(with details of treatment as per IS). The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 750mm from the finished ground level.For provision of treated earth-pit and untreated earth pit, refer the specification for designing. Provision of water taps inside the switch yard areas and peripheral treated and un-treated earth pit are required to be provided for watering the treated earth pits. The no. of treated and un treated earth pits are to be done as per the practice and as indicated in the drawing for different equipments. This is as per approved drawing and specification. spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision.
a | 75 x 10 mm Hot Dip Galvanized GI strip | Rmt | 500
b | 50 x 6 mm Hot Dip Galvanized GI strip | Rmt | 250
c | 25 x 6 mm Hot Dip Galvanized GI strip | Rmt | 100
d | 50MM GI PIPE FOR TREATED EARTH PIT ELECTRORDE WITH CHAMBER AND COVER | Rmt | 35
16 | EARTHING TAPES/ WIRES:
Supply and laying of following size Electrolyte grade Copper / Hot dip GI strip including all fixing accessories for laid inside the building with all necessary interconnections with earth station and equipments. end terminated with suitable copper lugs ,copper fixing hardware's. Below ground with civil excavation works , Below ground joints should be welded / Brazed only.
16.01 | Hot dip galvanized 50 x 6 mm GI tape with GI fixing hardware's. | Rmt | 150
16.02 | Hot dip galvanized 40 x 6 mm GI tape with GI fixing hardware's. | Rmt | 150
16.03 | Hot dip galvanized 25 x 6 mm GI tape with GI fixing hardware's. | Rmt | 200
16.04 | 8 SWG Copper wire ETP Grade material (as per IS:191) with copper fixing hardware's. | Rmt | 85
16.05 | 25 x 3 mm copper tape ETP Grade material (as per IS:191) with copper fixing hardware's. | Rmt | 100
16.06 | 25 x 6 mm copper tape ETP Grade material (as per IS:191) with copper fixing hardware's. | Rmt | 100
16.07 | 8 SWG Hot Dip GI wire | Rmt | 85
17 | H.T. 11 KV (E) XLPE Aluminum Armoured Cable :
Supply, laying, testing and commissioning of following size 3-core-11 KV Earthed HT XLPE insulated Aluminum armoured conductor under ground cable, shall be laid in built up cable trench / already laid RCC Hume pipe / on cable tray / in Excavated ground at a depth of 1000mm below From Finished ground level . The cable shall conform to IS 7098/ Part II.and as on date latest revision in IS standards
Note: Excavation and refilling of any type of earth soil, with supply and providing cable protection of half cut heavy duty Hume pipe with sand bed and top including C.I cable route marker will be operated under schedule heading of "Civil Works for outdoor cable laying".
[ MAKES : Universal / CCI-Tropodur / KEI / RPG / RR )
17.01 | 3-Core x 300 Sqmm 11 KV (E) XLPE Aluminum Armoured Cable - | Rmt | 150
18 | H.T. Cable End Termination :
Supply , providing ,testing and commissioning of 11KV (E) HT cable termination kit for indoor/ outdoor Heat shrinkable end termination kit suitable for the HT XLPE cable with all sundry material like BI-metallic Lugs using crimping , including Earthing of termination kit etc. full set complete.
[ MAKE: RAYCHEM ]
18.01 | 3-Core x 300 Sqmm 11KV (E) XLPE Aluminum Armoured Cables indoor End Termination : | No | 2
18.02 | 3-Core x 300 Sqmm 11KV (E) XLPE Aluminum Armoured Cables Out door End Termination : | No | 2
18.03 | 3-Core x 300 Sqmm 11 KV (E) XLPE Aluminum Armoured STRAIGHT THROUGH JOINT kit full set complete as required | No | 1
19 | GUY/ STAY SET
| Supply and fixing of guy set Comprising of 7/9 Swg wire with 15/19mm Dia 1.8 Mtrs long anchor rod turn buckle with eye bolt and nut for support the pole with insulator at 3 Mtrs level from ground level with all other necessary accessories with including all civil works like digging & refilling with RCC foundation. | No | 5
20 | MISCELLANEOUS WORKS :
20.01 | Supplying & Erection of 11 kV danger boards, as per STATE ELECTRICITY BOARD requirement. | No | 1
20.11 | Supplying & Erection of Rubber mats of 11 KV grade 2.0 Meters (L) x 1.0 Meters and of sufficient minimum 12mm thickness as required by the Electrical Inspectorate and confirming to IS 5424. | No | 1
20.21 | Supply and Installation of 5KG capacity ABC type fire extinguishers complete with mounting brackets, spray nozzles, connecting pipes, "OPEN / CLOSE" valves with all other necessary accessories complete as required. (make: USHA, fire pro). or equivalent of approved ISI make. | No | 1
20.31 | supply and providing of 11KV grade hand gloves with chalk powder including suitable weather proof transparent box with lock and key | No | 1
20.41 | Supply and providing of First Aid Box as per IS standard. | No | 1
20.51 | Supply and providing 4 nos of red color painted Fire buckets round bottom of 9 Liters capacity filled with dry sand with including suitable angle iron support red color painted. | No | 1
20.61 | Supply and Fixing of shock treatment Chart ( English & local state language ) as per CEIG /CEA standard with laminated frame. | No | 1
20.71 | Supply and providing Electrical As built single line diagrams (As Built scheme ) with laminated frame. | No | 1
TOTAL COST
GRAND TOTAL OF SUPPLY AND ERECTIONS ====>
TOTAL VALUE OF E.D
TOTAL VALUE OF CST
TOTAL VALUE OF VAT
TOTAL VALUE OF SER. TAX
GRAND TOTAL INCLUSIVE OF ALL DUTIES & TAXES
Note :
OHL poles and DP structures pits excavation , foundation should be inclusive of the quoted cost.
quoted cost should inclusive of pole identification number
11KV Aerial bunched cable cost should be incclusive of cost quoted
GI /Aluminium cable clamp should be used for the HT cable down drop from OHL ,poles ,DP structure to Ground , looping etc , the cost for this clamp and fixing hardware should be included in the cables RMT.
the quoted cost should included. Spiral Coil Earthing to be used for all poles
quoted cost should inclusive of all taxes , duty ,octroi, transport etc
EXCLUSION OF THE ITEMS
MASONARY CABLE TRENCH
based on Road layout this BOQ prepared , If any changes in road layout will affect the Drawings as well qty
| SIGNATURE OF CLIENTS WITH SEAL | [6 empty] | SIGNATURE OF BIDDER WITH SEAL

## Street light
| SEMAC CONSULTANTS PVT LTD, | CLIENT : M/s MEGA FOOD PARK PVT LTD
| ENGINERING DESIGN CONSULTANTS | Project : PROPOSED FOOD PARK DEVELOPMENT AT WAHEGAON VILLAGE , PAITHAN TALUKA , AURANGABAD
| ELECTRICAL DEPARTMENT - HYDERABAD - TELANGANA STATE [India] | Subject : TENDER BOQ FOR EXTERNAL LIGHTING WORKS OF THE PROPOSED MEGA FOOD PARK PVT LTD
| ISO 9001 : 2008 Certified Company | REV NO : R2 ; Date : 24.09.15 ; Job No : H-13-14/021 ; Doc No - 401
|  |  |  | SUPPLY | [6 empty] | ERECTION
SL.No | DESCRIPTION OF WORK | UNIT | QTY | BASIC RATE | ED | CST | VAT |  | Net Supply RATE | Net Supply AMOUNT | BASIC RATE | SER. TAX | Net Erection RATE | Net Erection AMOUNT
| Percentage of taxes and Duties => | [10 empty] | 12.36%
PART- C : STREET / ROAD LIGHTING
1 | STREET LIGHTING @ 30 MTRS INTERVAL
MAKE : BAJAJ / CG
1.01 | Supply and erection testing and commissioning of Hot Dip Galvanized internally and externally 70 micron DFL GI Single Section Octagonal pole 9 mtrs Long with Bottom 175mm A/F, top 70 mm A/F made up of 3 or 4 mm thick HT sheet along with 275 x 275 x 16 mm thick base plate whole item suitable to with stand for wind speed 169 km /hrs with Earthing studs, with in build TP+N+E loop-in & loop-out smart pack junction box with 3 core heavy duty 2.5 sqmm copper wire from smart box to lamps , 6A SP MCB and 20A 8 Nos terminals should be inside the base compartment of pole and Suitable to Terminate the loop in loop out cables. with 3mm thick heavy duty 60mm /100 mm dia PVC Long Bend pipe, Spiral coil earthing by 8 SWG GI wire with 25 mm dia B glass GI pipe of 600 mm length for Spiral coil earthing . [ BAJAJ Cat No: BOP-BOP-9030] | No | 100
0
1.02 | Excavation of outdoor pole Foundation pit at a depth of 2000 mm below the Ground Level which includes excavation of any type of soil as per site condition and supply and providing reinforced 600 x 600 x 2000 mm deep RCC M20/M25 Civil foundation with necessary "U" Bolts & Nuts suitable for wind speed 169 km /hrs as per detail of civil foundation drawings approved by consultants . [ Actual deep should be as per structural designer consultant ] | No | 100
0
1.03 | Supply and erection testing and commissioning of Hot Dip Galvanized internally and externally 65 to 70 micron DFL GI 1.0 / 0.5 meters long single cross Arm bracket suitable to the above pole ,pole cap bolt nut etc | No | 4
0
1.04 | Supply and erection testing and commissioning of Hot Dip Galvanized internally and externally 65 to 70 micron DFL GI 1.5 meters long single cross Arm bracket suitable to the above pole ,pole cap bolt nut etc | No | 35
0
1.05 | Supply and erection testing and commissioning of Hot Dip Galvanized internally and externally 65 to 70 micron DFL GI 1.0 / 0.5 meters long Double cross Arm bracket suitable to the above pole ,pole cap bolt nut etc | No | 4
0
1.06 | Supply and erection testing and commissioning of Hot Dip Galvanized internally and externally 65 to 70 micron DFL GI 1.5 meters long Double cross Arm bracket suitable to the above pole ,pole cap bolt nut etc | No | 57
0
2 | LIGHT FIXTURES WITH LAMPS |  | 0
0
2 | Supply, installation, testing & Commissioning of the following types fittings shall be with energy efficient complete with low loss Electronic ballast , igniter,starters,controlgear, connecting wire with Lamps, pf improvement capacitors for Lamps, all prewired up to the terminal block ,the rates quoted shall include all other accessories complete as required for suspending the lights, fans to the required level [ Make : Wipro / PHILIPS ] |  | 0
0
2.01 | Supply, installation, testing and commissioning of 132 W LED light fixture fitting along with all accessories Such as Gear Box , lamps etc as required with all fixing accessories ( Wipro CAT No: LR10-132-XXX-57 -XX ) | No | 165
0
2.02 | Supply, installation, testing and commissioning of 250W MH light fixture fitting along with all accessories Such as Gear Box , lamps etc as required with all fixing accessories ( Wipro CAT No:- WSH 50250 ) | No | 1
0
2.03 | Supply, installation, testing and commissioning of 250W MH light fixture fitting along with all accessories Such as Gear Box , lamps etc as required with all fixing accessories ( Wipro CAT No:- WSH 42250 ) | No | 10
0
2.04 | Supply, installation, testing and commissioning of 250W MH Flood light fixture fitting along with all accessories Such as Gear Box , lamps etc as required with all fixing accessories (philips CAT No:- MWF 331 1 X HPITP 250W A) | No | 20
0
2.05 | Supply, installation, testing and commissioning of 0.3 MTRS height suitable dia 50 mm dia B class GI pipe to be embedded in gate wall with 25 mm dia PVC bent Pipes for incoming and outgoings cables, with painting of two coats of Zinc chromate primer and two coats of Aluminum paint externally for length above the wall with weather proof Junction box consisting of 6A SP MCB, 20A 4 way Terminal box. The Junction box shall be of weather proof phase and neutral loop-in and loop-out box as per specifications/drawings The wiring from Junction box to Light fixture shall be carried out with 3core 2.5sq.mm flexible copper cable. | SET | 4
0
2.06 | Supply, installation, testing and commissioning of 85 W CFL GATE light fitting along with all accessories such as Gear box, lamps etc as required with all fixing accessories ( BAJAJ CAT NO: BNCL 85 RF CFL CLEAR ACRYLIC COVER ) | No | 8
2.07 | Supply and erection testing and commissioning of DECORATIVE wall mounted type Name board light fitting along with all accessories such as Gear box, lamps etc as required with all fixing accessories (BAJAJ CAT NO: PALU BASE 169243 ; BM GN 300WH 169223) or As per Architects / clients Selection and approved make. | No | 1
0
2.08 | Supply, installation, testing and commissioning of weather proof [ IP-66 ] junction box with full set complete with all fixing Hard wares ( Hensel CAT.NO KF 9105 ) or equivalent of approved make. | No | 4
3 | EARTHING : |  | 0
0
3.1 | SUPPLY & Providing C.I PIPE Earth station, with 100 mm internal dia 13mm thick C.I pipe 3 mtr long CI pipe with 2 runs of 50 x 6 mm Hot Dip Galvanized GI strips of each 3 Meter long with including Excavation of earth pit in any type of soil and construction of 230mm thick brick trough (450 mm length x 450mm wide x 450 inner trough clearance ), providing meshed funnel, CI heavy duty ISI approved Square type cover , C.I heavy duty rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper /bimetallic/ GI bolt nut washer etc, completely as per IS 3043, 1987 or latest revision. [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | 4
0
3.2 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 3 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. )[ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No | 2
0
3.21 | Supply and Providing Substation earth-mat Design, engineering, supply inclusive of corrosion protection measures if any,laying of earth-mat conductors of Hot dip galvanized flats of size 75X10 mm to the approval of Project Manager, excavation, welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc of ground conductors along with risers (of size 50X6 mm GI flats) etc back filling and good compaction,grounding driven rods(40 mm MS solid rod),perforated GI pipes for treated earth pits(with details of treatment as per IS). The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 750mm from the finished ground level.For provision of treated earth-pit and untreated earth pit, refer the specification for designing. Provision of water taps inside the switch yard areas and peripheral treated and un-treated earth pit are required to be provided for watering the treated earth pits. The no. of treated and un treated earth pits are to be done as per the practice and as indicated in the drawing for different equipments. This is as per approved drawing and specification. spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision.
a | 75 x 10 mm Hot Dip Galvanized GI strip | Rmt | 100
b | 50 x 6 mm Hot Dip Galvanized GI strip | Rmt | 100
c | 25 x 6 mm Hot Dip Galvanized GI strip | Rmt | 50
d | 50MM GI PIPE FOR TREATED EARTH PIT ELECTRORDE WITH CHAMBER AND COVER | Rmt | 35
4 | EARTHING TAPES/ WIRES: |  | 0
0
| Supply and laying of following size Electrolyte grade Copper / Hot dip GI strip including all fixing accessories for laid inside the building with all necessary interconnections with earth station and equipments. end terminated with suitable copper lugs ,copper fixing hardware's. Below ground with civil excavation works , Below ground joints should be welded / Brazed only. |  | 0
4.1 | Hot dip galvanized 40 x 6 mm GI tape with GI fixing hardware's. | Rmt | 100
0
4.2 | Hot dip galvanized 25 x 6 mm GI tape with GI fixing hardware's. | Rmt | 100
0
4.2 | 8 SWG Copper wire ETP Grade material (as per IS:191) with copper fixing hardware's. | Rmt | 40
0
5 | AREA LIGHTING PANEL (WEATHER Proof TYPE out door PEDESTAL MOUNTED ) |  | 0
| (MAKE : SIEMENS / SCHNEIDER /LEGRAND ) |  | 0
| INCOMER |  | 0
| 125A, TPN, 415V, 25 KA Molded Case Circuit Breakers with Thermal Magnetic based releases with 125 A 3P contactors-1 no ,24 hours day timer-1 no, including ON/ OFF indication lamps-6 Nos. And Sensor or light Dependent resistors (LDR) to automatic ON & Off based on Sun light level |  | 0
| Area Light Circuit Should be connected with one timer switches to control all lights between 6 PM to 6 AM. |  | 0
| METERING |  | 0
| Load Manager with measuring parameters of Voltage, Current, Frequency (Conzerv Cat Log No: EM 6400 with Rs485). |  | 0
| 125 /5A, CL - 1.0, 10VA Resin Cast Current Transformers - 3 No |  | 0
| 2A, TPN MCB -1No. |  | 0
| Auto manual Selector switch-2 |  | 0
| 24 hours day timer-2 no |  | 0
| LED Type Indication Lamps for R, Y, B Phase Indication and Breakers ON / OFF / TRIP Indication |  | 0
| BUS BAR : |  | 0
| 125 A,Electrolyte Grade TPN+E Aluminum Bus bars with 0.8A/Sq.mm Current density. |  | 0
| OUTGOINGS : |  | 0
| 10-32A, DP, MCB(10 KA) - 12 Nos |  | 0
63A, TP, MCB(10KA) - 4 Nos
| 10-32A, TP, MCB(10KA) - 12 Nos | No | 2
0
6 | POWER AND Control CABLES : |  | 0
0
| Supply, laying, testing and commissioning of following size 1.1KV Grade Aluminum XLPE / Copper Conductor XLPE insulated PVC extruded Sheathed Armored under ground cable and shall be laid in built up cable trench/ already laid RCC Hume pipe or on cable tray (indoor/outdoor). with all installation materials as required. The cable shall conform to IS 1554/ Part I. For buried cables, the excavation work will be included under the heading "Civil works for outdoor cable laying." |  | 0
| ( MAKES: UNIVERSAL / CCI Tropodur / KEI /RR /RPG ) |  | 0
6.01 | 3.5 Core x 95 Sqmm XLPE AL.AR Cable | Rmt | 50
0
6.02 | 3.5 Core x 70 Sqmm XLPE AL.AR Cable | Rmt | 550
0
6.03 | 3.5 Core x 50 Sqmm XLPE AL.AR Cable | Rmt | 550
6.04 | 3.5 Core x 35 Sqmm XLPE AL.AR Cable | Rmt | 50
0
6.05 | 4 Core x 25 Sqmm XLPE AL.AR Cable | Rmt | 1100
0
6.06 | 4 Core x 16 Sqmm XLPE AL.AR Cable | Rmt | 2200
0
6.07 | 4 Core x 10 Sqmm XLPE AL.AR Cable | Rmt | 3800
0
6.08 | 4 Core x 6 Sqmm XLPE AL.AR Cable | Rmt | 1200
0
6.09 | 4 Core x 2.5 Sqmm PVC CU.AR.Cable | Rmt | 200
0
7 | CABLE END TERMINATIONS : |  | 0
0
7 | Supply and Providing cable end terminations with Double compression type SS Gland, Bi-metallic Heavy duty lugs , insulation tape, identification Aluminum Engraved tags etc.With including Gland Earthing, Drilling for Gland complete as required. |  | 0
.(Make-HMI/ COMET , Lugs: DOWELLS/HEX).
7.01 | 3.5 Core x 95 Sqmm XLPE AL.AR Cable | No | 2
0
7.02 | 3.5 Core x 70 Sqmm XLPE AL.AR Cable | No | 2
0
7.03 | 3.5 Core x 50 Sqmm XLPE AL.AR Cable | No | 2
7.03 | 3.5 Core x 35 Sqmm XLPE AL.AR Cable | No | 2
0
7.04 | 4 Core x 25 Sqmm XLPE AL.AR Cable | No | 20
0
7.05 | 4 Core x 16 Sqmm XLPE AL.AR Cable | No | 20
0
7.06 | 4 Core x 10 Sqmm XLPE AL.AR Cable | No | 200
0
7.07 | 4 Core x 6 Sqmm XLPE AL.AR Cable | No | 100
0
7.08 | 4 Core x 2.5 Sqmm PVC CU.AR.Cable | No | 20
0
8 | CIVIL WORKS FOR OUTDOOR CABLE LAYING : |  | 0
0
| supply , Excavation of outdoor cable trenches at a depth specified below From Ground Level with including excavation at any type of soil as per site condition requirements and providing sand layer bed cushioning for cable, providing HALF CUT HEAVY DUTY HUME PIPE for entire length covering and refilling the trench and making good surface as required. quoted cost inclusive of Providing HT / LT cable route marker at every 15 Mtrs distance. |  | 0
8.01 | Trench of width 600mm & depth 600 mm. | Rmt | 400
0
8.02 | Trench of width 450mm & depth 600 mm. | Rmt | 4050
0
8.03 | Trench of width 300mm & depth 600mm. | Rmt | 150
TOTAL COST
GRAND TOTAL OF SUPPLY AND ERECTIONS ====>
TOTAL VALUE OF E.D
TOTAL VALUE OF CST
TOTAL VALUE OF VAT
TOTAL VALUE OF SER. TAX
GRAND TOTAL INCLUSIVE OF ALL DUTIES & TAXES
Note :
a) based on Road layout this BOQ prepared , If any changes in road layout will affect the Drawings as well qty
b) quoted cost should inclusive of pole identification number
c ) quoted cost should inclusive of all taxes , duty ,octroi, transport etc
EXCLUSION OF ITEMS
MASONARY CABLE TRENCH
Feeder pillar panels - pedestal / FOUNDATION works ,
| SIGNATURE OF CLIENTS WITH SEAL | [6 empty] | SIGNATURE OF BIDDER WITH SEAL

## LIASIONING WORKS
| SEMAC CONSULTANTS PVT LTD, | CLIENT : M/s MEGA FOOD PARK PVT LTD
| ENGINERING DESIGN CONSULTANTS | Project : PROPOSED FOOD PARK DEVELOPMENT AT WAHEGAON VILLAGE , PAITHAN TALUKA , AURANGABAD
| ELECTRICAL DEPARTMENT - HYDERABAD - TELANGANA STATE [India] | Subject : TENDER BOQ FOR ROAD LIASONING WORKS OF THE PROPOSED MEGA FOOD PARK PVT LTD
| ISO 9001 : 2008 Certified Company | Date : 24.09.15 ; Job No : H-13-14/021 ; Doc No - 401 ;REV NO : R2 ;
|  |  |  | SUPPLY | [6 empty] | ERECTION
SL.No | DESCRIPTION OF WORK | UNIT | QTY | BASIC RATE | ED | CST | VAT |  | Net Supply RATE | Net Supply AMOUNT | BASIC RATE | SER. TAX | Net Erection RATE | Net Erection AMOUNT
| Percentage of taxes and Duties => | [10 empty] | 12.36%
PART- D : MSEDCL LIASIONING WORKS
1 | CEIG APPROVAL :
| Liasioning with CEIG with Preparation of drawings as per Dy. CEIG standards and geeting drawing approval transformer, DG, UPS, Stabilizer HT / LT installation, lifts etc. That is total project Electrification work , Filing the completion report of works to the Electrical Inspectorate authorities, getting the inspection done at site, after that filing the rectification report with necessary rectification of defect pointed out By CEIG and getting the final approval from Electrical Inspectorate authorities and getting the safety certificate and charging the Electricity Board line portion of the work etc. Single window agency approval will be furnished by Client. | Lsm | 1
2 | STATE EB LOAD SANCTION & DEMAND APPROVAL
| Liasioning with STATE ELECTRICITY BOARD - Authorities for getting the Load sanction And filling the neceessry Forms ,documents etc Single window agency approval will be furnished by Client. The contractor has to get the load sanction ,bring the supply line up to the consumer premisses,and charging the EB supply. (all Development charge,security deposit,sevice charge /supervison charges and fees of MSEDCL will be paid by costomer based on orginal bill value , the payment will be paid to the contractor after handing over the orginal bill or EB receipts. in the bill clearly client address and the towards the fees for what purpose Paid should be clearly mentioned . | Lsm | 1
TOTAL COST
GRAND TOTAL OF SUPPLY AND ERECTIONS ====>
TOTAL VALUE OF E.D
TOTAL VALUE OF CST
TOTAL VALUE OF VAT
TOTAL VALUE OF SER. TAX
GRAND TOTAL INCLUSIVE OF ALL DUTIES & TAXES
Note :
a) based on Road layout this BOQ prepared , If any changes in road layout will affect the Drawings as well qty
b) quoted cost should inclusive of all taxes , duty ,octroi, transport etc
EXCLUSION OF ITEMS
Electricity Boards : Development charge ,security deposit , service charge ,load sanctioning fee , meter deposits etc ... Not considered
MHSEB External scope of work & specification will be issued by APSEB statutory authorities on completion of their estimation , the work to be executed as per authorities guideline only.
Right of way and land acquisition & Any other approval other than CEIG
National highway approval ETC not considered
| SIGNATURE OF CLIENTS WITH SEAL | [6 empty] | SIGNATURE OF BIDDER WITH SEAL

## TP
| SEMAC CONSULTANTS PVT LTD, | CLIENT : M/s MEGA FOOD PARK PVT LTD
| ENGINERING DESIGN CONSULTANTS | Project : PROPOSED FOOD PARK DEVELOPMENT AT WAHEGAON VILLAGE , PAITHAN TALUKA , AURANGABAD
| ELECTRICAL DEPARTMENT - HYDERABAD - TELANGANA STATE [India] | Subject : TENDER BOQ FOR LAN&TP NET WORKS OF THE PROPOSED MEGA FOOD PARK PVT LTD
| ISO 9001 : 2008 Certified Company | Date : 24.09.15 ; Job No : H-13-14/021 ; Doc No - 401 -REV NO : R2 ;
|  |  |  | SUPPLY | [6 empty] | ERECTION
SL.No | DESCRIPTION OF WORK | UNIT | QTY | BASIC RATE | ED | CST | VAT |  | Net Supply RATE | Net Supply AMOUNT | BASIC RATE | SER. TAX | Net Erection RATE | Net Erection AMOUNT
| Percentage of taxes and Duties => | [10 empty] | 12.36%
PART- E : DATA & TELE PHONE DISTRIBUTION WORKS
1 | OFC WORKS
1.01 | Supply, laying, testing and commissioning of 12 core SM Outdoor OFC Cable [MAKE : Molex ] 12-core, Single Mode, Corrugated Steel tape Armour, Loose-tube, Fully water blocked core ,E glass Yarns, Out door fiber cable fully conforming to ITU-T G.652.D And/OR IEC 60793-2-50 C1.3 standard | RMT | 4500
1.02 | Supply, laying, testing and commissioning of Pig Tail (1 m long) as per Tec Specification No. G/OFJ- 01 / 03 Jun'99 with latest amendment. [MAKE : Molex ] | No | 240
1.03 | Supply, laying, testing and commissioning of Molex 6 Pak SC Duplex Adaptor Plate SM Loaded [MAKE : Molex ] | No | 44
1.04 | Supply, laying, testing and commissioning of Molex Blank plate [MAKE : Molex ] | No | 6
1.05 | Supply, laying, testing and commissioning of Molex 48 Port Standard Grade fiber Enclosure, 2U - Unloaded [MAKE : Molex ] | No | 4
1.06 | Supply, laying, testing and commissioning of Molex 24 Port Standard Grade fiber Enclosure, 1U - Unloaded [MAKE : Molex ] | No | 4
1.07 | Supply, laying, testing and commissioning of Molex SC-LC / SC-SC Duplex Ptach cord SM 2 Mtr length [MAKE : Molex ] | No | 110
2 | RACKS:
2.01 | Supply, laying, testing and commissioning of 42 U 19" 800 X 800 Network Rack with necessary accessories | No | 1
2.02 | Supply, laying, testing and commissioning of Outdoor Metal Enclosure H36"x W36"x D 12" Network Rack with necessary accessories | No | 6
3 | Project Management Charges
3.01 | Project Management Charges for entire DATA works | LSM | 1
4 | VOICE WORKS -TELEPHONE CABLES / JELLY FILLED CABLES :
Supply and laying, Testing of telephone cables armoured annealed tinned copper conductor and petroleum jelly filled with polythene outer jackets conforming to P&T specification. The method of Telephone cables shall be run in a separate trench at least 600 mm away from other power cables. The civil works for excavation will be included under heading "Civil Works for Outdoor Cable Laying This rate shall include cable end terminations also using kits cable glands cable lugs etc as required complete.
NOTE:- The cable sizes & lengths for Telephone cables, conduits & wires / LAN conduits are only tentative. However they may vary as per the site conditions & actual requirements
4.01 | 10 Pair Armoured annealed tinned copper conductor cable and petroleum jelly filled | RMT | 100
4.02 | 50 Pair Armoured annealed tinned copper conductor cable and petroleum jelly filled | RMT | 300
4.03 | 100 Pair Armoured annealed tinned copper conductor cable and petroleum jelly filled | RMT | 2000
4.04 | 150 Pair Armoured annealed tinned copper conductor cable and petroleum jelly filled | RMT | 1500
5 | TELEPHONE JUNCTION BOXES :
Supply and installation of outdoor type krone connectors terminal box with including krone connectors ,locking arrangements full set complete with All fixing hardwares .
5.01 | 10 Pair Telephone junction MDF box with krone connectors | No | 4
5.02 | 50 Pair Telephone junction MDF with krone connectors | No | 2
5.03 | 100 Pair Telephone junction MDF with krone connectors | No | 6
5.04 | 150 Pair Telephone jjunction MDF with krone connectors | No | 2
6 | Project Management Charges
6.01 | Project Management Charges for entire Tele phone system | LSM | 1
7 | CIVIL WORKS FOR OUTDOOR CABLE LAYING :
supply , Excavation of outdoor cable trenches at a depth specified below From Ground Level with including excavation at any type of soil as per site condition requirements and providing sand layer bed cushioning for cable, providing HALF CUT HEAVY DUTY HUME PIPE for entire length covering and refilling the trench and making good surface as required. quoted cost inclusive of Providing HT / LT cable route marker at every 15 Mtrs distance.
7.01 | Trench of width 600mm & depth 750 mm. | Rmt | 750
7.02 | Trench of width 450mm & depth 750 mm. | Rmt | 3000
7.03 | Trench of width 300mm & depth 750mm. | Rmt | 100
8 | EARTHING
8.01 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 6 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 500 KVA Transformer Neutral earthing )[ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No. | 5
9 | ETP Grade EARTHING TAPES (Electrolyte Grade )
Supply and laying of following size earth strips including excavation and refilling of earth when laid in ground if required with all fixing accessories when laid on the wall/ Cable tray with necessary interconnections with earth station and equipments. Including copper hardware items. strips joints should be copper welded or brazed.
9.01 | 25x 3 mm Copper Tape | Rmt | 130
TOTAL COST
GRAND TOTAL OF SUPPLY AND ERECTIONS ==>
TOTAL VALUE OF E.D
TOTAL VALUE OF CST
TOTAL VALUE OF VAT
TOTAL VALUE OF SER. TAX
GRAND TOTAL INCLUSIVE OF ALL DUTIES & TAXES
Note :
A ) if any change in ROAD layout will affect the OFC and TP cable length
B) quoted cost should inclusive of all taxes , duty ,octroi, transport etc
EXCLUSION OF ITEMS
MASONARY CABLE TRENCH
from EXTERNAL SERVICE PROVIDERS INCOMING OFC CABLE WITH ALL ACCESSORIES
civil works required Exchange room and 6 nos of mini exchange rooms
Each individual leasable plots OFC and TP cables
| SIGNATURE OF CLIENTS WITH SEAL | [6 empty] | SIGNATURE OF BIDDER WITH SEAL

## SOLAR
| SEMAC CONSULTANTS PVT LTD, | CLIENT : M/s MEGA FOOD PARK PVT LTD
| ENGINERING DESIGN CONSULTANTS | Project : PROPOSED FOOD PARK DEVELOPMENT AT WAHEGAON VILLAGE , PAITHAN TALUKA , AURANGABAD
| ELECTRICAL DEPARTMENT - HYDERABAD - TELANGANA STATE [India] | Subject : TENDER BOQ FOR SOLAR LIGHTING WORKS OF THE PROPOSED MEGA FOOD PARK PVT LTD
| ISO 9001 : 2008 Certified Company | Date : 24.09.15 ; Job No : H-13-14/021 ; Doc No - 401 ; REV NO : R2 ;
|  |  |  | SUPPLY | [6 empty] | ERECTION
SL.No | DESCRIPTION OF WORK | UNIT | QTY | BASIC RATE | ED | CST | VAT |  | Net Supply RATE | Net Supply AMOUNT | BASIC RATE | SER. TAX | Net Erection RATE | Net Erection AMOUNT
| Percentage of taxes and Duties => | [10 empty] | 12.36%
PART- F : [ SOLAR LIGHTING SYSTEM ]
1 | SOLAR STREET LIGHTING - - as per MNRE
1.01 | Supply and erection testing and commissioning of Hot Dip Galvanized internally and externally 70 micron DFL GI Single Section Octagonal poles of 7 mtrs Long . with Bottom 130 mm A/F, top 70 mm A/F made up of 3mm thick HT plate along with 200X200X12mm thick base plate suitable for wind speed 169 km /hrs with Earthing studs, in build TP+N+E loop-in and loop-out smart pack junction box with 6A SP MCB and 20A 8 Nos terminals should be inside the base compartment of pole and Suitable to Terminate the 4C X 4 Sqmm CU AR cable. loop in loop out 3mm thick heavy duty 60mm dia PVC pipe cost should inclusive of Spiral coil earthing by 8 SWG GI wire with 32 mm B glass GI pipe of 750 mm length for Spiral coil pole earthing . (MAKE BAJA Cat No: BOP-7 030) | No | 52
1.02 | Excavation of outdoor pole Foundation pit at a depth of minimum 1000mm below the Ground Level which includes excavation of any type of soil as per site condition and supply and providing reinforced 500 x 500 x 1200 mm deep RCC Civil foundation with necessary "U" Bolts & Nuts suitable for wind speed 169 km /hrs as per detail of civil foundation drawings approved by consultants . ( actual deep should be as per structural design /bajaj drawing it will vary ) | No | 52
1.03 | Supply and erection testing and commissioning of Hot Dip Galvanized internally and externally 65 to 70 micron DFL GI 1.0 mtrs long single cross Arm bracket suitable to the above pole ,pole cap bolt nut etc | No | 5
1.04 | Supply and erection testing and commissioning of Hot Dip Galvanized internally and externally 65 to 70 micron DFL GI 1.5 mtrs long single cross Arm bracket suitable to the above pole ,pole cap bolt nut etc | No | 47
2 | HYBRID SOLAR STREET LIGHTING -
Supply, installation, testing & Commissioning of MPPT BASED CHARGE with Hybrid system solar street lighting system with High efficiency Mono Multi Crystalline Confirming to IEC standards , Low maintenance positive tubular plate lead Acid battery Rate of discharge Suitable for 3 days system , MPPT BASED Charge controller 12V, the entire lighting system is weather proof IP 66 /67 ,Charge Controller - MPPT (microprocessor based) , AUTONOMY - 2 DAYS ; Enclosure -IP65 ; Solar cells- Multi crystalline silicon, Lead-acid tubular battery of low maintenance, - Standards :EN50530 for MPPT performance ,Solar Panel:IEC 61215,Electronics, EN50530 : MPPT Performance evaluation , IEC62124 : Solar standalone system performance ,IEC61347-2-13 : LED driver safety ,IEC 62384 : LED driver performance, CISPR 15 : Radio disturbance characteristics, IEC61547 : EMC Immunity requirements ,IEC60598 : [ MAKE : BAJAJ / CG / PHILIPS ]
2.01 | HYBRID 60W Solar LED street Light Luminaire comprises of die cast Aluminium housing powder coated in graphite grey and toughened glass with IP 65 Protection. fitted with gasket & accessories- IP65-Single luminary. Lumens minimum output-130 W .In- built dusk to dawn 2DAYS , automatic operation, Solar Panel PV Module: 12V/140Wp Poly Crystalline Type - 2nos , Battery: 135Ah-12V Tubular Battery - 2 Nos Battery Box Enclosure made by SS-304 , Charge Controler: MPPT type charge controller full set complete with all fixing hard wares [ MAKE : BAJAJ / CG /PHILIPS ] | No | 52
2.02 | HYBRID 90W Solar LED street Light Luminaire comprises of die cast Aluminium housing powder coated in graphite grey and toughened glass with IP 65 Protection. fitted with gasket & accessories- IP65-Single luminary. Lumens minimum output-130 W .In- built dusk to dawn 2DAYS , automatic operation, Solar Panel PV Module: 12V/140Wp Poly Crystalline Type - 2nos , Battery: 150Ah-12V Tubular Battery - 4 Nos Battery Box Enclosure made by SS-304 , Charge Controler: MPPT type charge controller full set complete with all fixing hard wares [ MAKE : BAJAJ / CG /PHILIPS ] | No | 2
2.03 | set of user’s tool & tackles kit and operation &Maintenance manual as per - as per MNRE specs. Nodal Agencies [ MAKE : BAJAJ / CG /PHILIPS ] | SET | 5
TOTAL COST
GRAND TOTAL OF SUPPLY AND ERECTIONS ====>
TOTAL VALUE OF E.D
TOTAL VALUE OF CST
TOTAL VALUE OF VAT
TOTAL VALUE OF SER. TAX
GRAND TOTAL INCLUSIVE OF ALL DUTIES & TAXES
Note :
A ) based on Road layout this BOQ prepared , If any changes in road layout will affect the Drawings as well qty
b) quoted cost should inclusive of all taxes , duty ,octroi, transport etc
C ) quoted cost should inclusive of all taxes , duty ,octroi, transport etc
EXCLUSION OF ITEMS
MASONARY CABLE TRENCH
LT cable for any Hybrid options
| SIGNATURE OF CLIENTS WITH SEAL | [6 empty] | SIGNATURE OF BIDDER WITH SEAL

## DG
| SEMAC CONSULTANTS PVT LTD, | CLIENT : M/s MEGA FOOD PARK PVT LTD
| ENGINERING DESIGN CONSULTANTS | Project : PROPOSED FOOD PARK DEVELOPMENT AT WAHEGAON VILLAGE , PAITHAN TALUKA , AURANGABAD
| ELECTRICAL DEPARTMENT - HYDERABAD - TELANGANA STATE [India] | Subject : TENDER BOQ DG SUPPLY DISTIBUTION WORKS OF THE PROPOSED MEGA FOOD PARK PVT LTD
| ISO 9001 : 2008 Certified Company | Date : 24.09.15 ; Job No : H-13-14/021 ; Doc No - 401 REV NO : R2 ;
|  |  |  | SUPPLY | [5 empty] | ERECTION
SL.No | DESCRIPTION OF WORK | UNIT | QTY | BASIC RATE | ED | CST | VAT | Net Supply RATE | Net Supply AMOUNT | BASIC RATE | SER. TAX | Net Erection RATE | Net Erection AMOUNT
| Percentage of taxes and Duties => | [9 empty] | 12.36%
PART- G : [ DG POWER BACK UP FOR CORE & INFRA STRUCTURE AREA ONLY ]
1 | PRIME POWER CONTINUOUS DUTY DG SETS
1.01 | Supply, Erection, Testing and commissioning of 415V, 3Ph., 50Hz. Prime duty following RATTING OF DG set with weather proof acoustic enclosure, electrical control panel. The diesel engine shall be complete with necessary control and safety devices as per IS/BS specifications. Noise level should be less than 70db.The engine shall be suitable for continuous operation of Generator duty, inclusive of fly wheel, flexible coupling, air cleaner, corrosion resistor, Radiator fan with guard, fuel pump, fuel filter, electronic governor, starting system with separate battery charger with 24V Batteries, voltage regulator, Instrument panel with RPM indicator, Exhaust silencer with cladding (residential) with First Fill up luboil , Protection against low lube oil pressure, high water temperature and with 990Ltrs. Capacity fuel tank, fuel lines from fuel tank to DG set, battery stand, anti vibration pads and the quoted cost should inclusive of first filling of lubricating oil and fuel oil for test. The Alternator shall be suitable for 415V 3phase,4wire, 50Hz 0.8 PF AC Supply operation and shall be able to deliver full load current at 100% Unbalanced load. The price should be inclusive of Canopy as per CPCB norms. (Note: For testing the DG Set required loads to be organized by respective vendor only.)
[ Make: Cuminns / CATER PILLAR ]
1.02 | same as above description With 100 KVA PRIME POWER DG SET With Auto main failure start panel [ SS building & Street lighting ] | No | 1
1.03 | same as above description With 250 KVA PRIME POWER DG SET With Auto main failure start panel - [ ware House ,MSME shead building ] | No | 1
1.04 | same as above description With 500 KVA PRIME POWER DG SET With Auto main failure start panel - [ Admin building ] | No | 1
1.05 | same as above description With 1250 KVA PRIME POWER DG SET - [ F&V building ] | No | 2
2 | EXHAUST SYSTEM :
Supply, Erection, Testing and commissioning of suitable Dia ( minimum 300mm Dia ) 6mm thick B Class MS pipe with flanges, fire fly gaskets, hardware, gladded with 50mm thick Glass wool insulation covered with 24SWG Aluminum sheet and provided with rain cap etc.., as per specification inclusive of all supports of wall, ceiling, etc.,
[ Make:- Jindal / TATA / Vizag ]
2.01 | Exhaust pipe including flexible from DG set covered by glass wool with Aluminum cladding etc., | No | 120
2.02 | Supply, Erection, Testing and commissioning of 1.0 meters long 20mm solid copper rod with air terminal with base plate full set complete . | No | 5
2.03 | Aviation Obstruction light fixture suitable for LED lamp with clear glass dome, lamp, in built Transformer and all other necessary accessories with 1.0 meter long 40mm Dia B-Class G.i pipe with supporting material complete as required. ( Phillips /WIPRO /BAJAJ /CG Make ] | No | 5
3 | POLLUTION CONTROL BOARD APPROVAL :
3.01 | Liasioning with Pollution Control Board Authorities for getting the sanction. Preparation of as built drawings as required standards for approval, Filling the completion report to the authorities, getting the inspection done at site, filling the reflection report, getting the approval from Pollution Control Boas authorities. Single window agency approval will be furnished by Client.( for All DG set) | LSM | QRO
4 | STEEL ITEMS
4.01 | Supply, fabrication, erection painting of all type of steel items (ISMC,ISMB,ISA,etc.., as required as per specification complete. Generally steel items For cable trays, BT's supporting arrangements, checkers plates above trenches and any other steel items not covered in other items of schedule of quantities. The quoted rate should inclusive of painting the steel items with two coats of red oxide primer and two coats of synthetic enamel paint of approved shade. | MT | 30
[ Make:- Jindal / TATA / Vizag ]
5 | FUEL SYSTEM :
Supply, Erection, Testing and commissioning of Fuel supply system with MS medium class pipe with flange & gas welded joint & pipe fittings like valves and other accessories complete as required as per technical specifications.
[ Make:- Jindal / TATA ]
5.01 | 20mm dia. | RMT | 30
5.02 | 25mm dia. | RMT | 30
5.03 | 32 mm dia. | RMT | 30
6 | AMF & SYNCHRONIZING PANEL EXTENDABLE TYPE
6.01 | Supply,erection, testing and commissioning of DG Sets With Auto Main Failure With Individual ACB , Load sharing , Load shedding and Auto mains failure Facility with built-in individual ACBs as incomers and outgoing of required capacity with the double voltmeter, double frequency meter & consisting of complete set of necessary Relays & Meters and following accessories. of complete set of necessary Relays & Meters.
Incoming :
a) 2000 A, TP, 65KA, Electrical Draw out type Air Circuit Breaker with Micro Processor Based releases for O/C, S/C, E/F,UV, & ST RELEASES along with TNC switch, Neutral power contactor -2 No (Siemens Cat Log no: 3WL 1220 & ETU 45 B).
METERING
Load Manager with measuring parameters of Voltage, Current, KWH, KW, KVAR, PF, Frequency -2No (Conzerv Cat Log No: EM 6400 with Rs 485).
2000/5A,CL -1 , 15VA Resin Cast Current Transformers - 6 Nos To meter .
32A-TP MCB -2 NO & 2A- TP,MCB-2 NO
LED Type Indication Lamps for R, Y, B Phase Indication and Breakers ON / OFF / TRIP/ Trip Lamps
Bus Bars :
4000A, Electrolyte Grade Aluminium ( TP+1N+1E) Bus bars with 0.8 A/Sq.mm Current density.
b) Start/stop/Trip controls with True RMS type Digital meters with LCD Displays & AMF Module.
c) Auto/ Manual Selector switch.
d) All the metering protection & controls
e) 1 No battery charger
f) Digital Ammeter
g) Digital Voltmeter
h ) Digital kWh meter
I) Digital kW meter
j) Digital Frequency meter
k) Digital PF meter
l) Current Transformers
m) Load Manager with measuring parameters of Voltage, Current, KWH, KW, KVAR, PF, Frequency - 2nos (Siemens Cat Log No: PAC 3100 with Rs485).
n) Current Transformers
o) Indicating lamps for "ON/OFF/ENGINE TRIP/POWER SHUT OFF/POWER ON/LOAD OFF/LOAD ON"
p) Earth Leakage Relay with Core Balanced Current Transformers.
q) Reverse Power relay
r) IDMT relay
s) REF relay
t) AMF / Synchronization / Load Dependent auto Stop / Start of Woodward relay
u) Annunciation Module with indication and hooters for the same with acknowledgement / reset Push Buttons. With annunciation windows 1)Low Lub Oil Pr, 2) High Water temp, 3) Over Speed,4) Battery Charger Fail,5) Auto Fail to Start, 6)Low Lub Oil Pr-Trip, 7) High Water temp-Trip 8) Over Speed-Trip 8) Bracket Trip on Fault.
OUTGOING
4000A, 4P, 65KA, Electrical Draw out type Air Circuit Breaker with Micro Processor Based releases for O/C, S/C, E/F,UV, & ST RELEASES along with TNC switch -1 No (Siemens Cat Log no: 3WL ).
| LED Type Indication Lamps for R, Y, B Phase Indication and Breakers ON / OFF / TRIP/ Trip Lamps | No | 1
7 | EARTH STATIONS:
7.01 | SUPPLY & Providing C.I PIPE Earth station, with 100 mm internal dia 13mm thick C.I pipe 3 mtr long CI pipe with 2 runs of 50 x 6 mm Hot Dip Galvanized GI strips of each 3 Meter long with including Excavation of earth pit in any type of soil and construction of 230mm thick brick trough (450 mm length x 450mm wide x 450 inner trough clearance ), providing meshed funnel, CI heavy duty ISI approved Square type cover , C.I heavy duty rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper /bimetallic/ GI bolt nut washer etc, completely as per IS 3043, 1987 or latest revision. [ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No. | 4
7.02 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 3 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 100 KVA Transformer Neutral earthing )[ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No. | 2
7.03 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 3 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 250 KVA Transformer Neutral earthing )[ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No. | 2
7.04 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 25 x 6 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 500 KVA Transformer Neutral earthing )[ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No. | 2
7.05 | Supply and Providing Copper Plate Earth station, with 600 X 600 X 3.15mm thick copper plate terminated with 2 runs of 60 x 6 mm copper strips of 3 M length with 100 mm internal dia 13mm thick C.I pipe 3 meter long CI pipe with including construction of 230mm thick brick trough (450 x 450 x 450 inner clearance ), providing meshed funnel, CI heavy duty cover , rib and other civil Engineering works, spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision. (for 1250 KVA Transformer Neutral earthing )[ C.I pipe make : Kapilansh Dhatu Udyog Pvt Ltd, model no : type D ] | No. | 2
7.06 | Supply and Providing Substation earth-mat Design, engineering, supply inclusive of corrosion protection measures if any,laying of earth-mat conductors of Hot dip galvanized flats of size 75X10 mm to the approval of Project Manager, excavation, welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc of ground conductors along with risers (of size 50X6 mm GI flats) etc back filling and good compaction,grounding driven rods(40 mm MS solid rod),perforated GI pipes for treated earth pits(with details of treatment as per IS). The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 750mm from the finished ground level.For provision of treated earth-pit and untreated earth pit, refer the specification for designing. Provision of water taps inside the switch yard areas and peripheral treated and un-treated earth pit are required to be provided for watering the treated earth pits. The no. of treated and un treated earth pits are to be done as per the practice and as indicated in the drawing for different equipments. This is as per approved drawing and specification. spreading a homogenous mixture of Pentonite around the plate, copper bolt nut etc, completely as per IS 3043, 1987 or latest revision.
a | 75 x 10 mm Hot Dip Galvanized GI strip | Rmt | 850
b | 50 x 6 mm Hot Dip Galvanized GI strip | Rmt | 350
c | 25 x 6 mm Hot Dip Galvanized GI strip | Rmt | 250
d | 50MM GI PIPE FOR TREATED EARTH PIT ELECTRORDE WITH CHAMBER AND COVER | Rmt | 45
8 | ETP Grade EARTHING TAPES (Electrolyte Grade )
Supply and laying of following size earth strips including excavation and refilling of earth when laid in ground if required with all fixing accessories when laid on the wall/ Cable tray with necessary interconnections with earth station and equipments. Including copper hardware items. strips joints should be copper welded or brazed.
8.01 | 25x 3 mm Copper Tape (for 100 KVA Neutral ear thing ) | Rmt | 50
8.02 | 25x 3 mm Copper Tape (for 250 KVA Neutral ear thing ) | Rmt | 100
8.03 | 25x 6 mm Copper Tape (for 500 KVA Neutral ear thing ) | Rmt | 120
8.04 | 60 x 6 mm Copper Tape (for 1250 KVA Neutral ear thing ) | Rmt | 150
8.05 | 25 x 6 mm Hot Dip Galvanized GI strip (for Body ear thing ) | Rmt | 400
8.06 | 50 x 6 mm Hot Dip Galvanized GI strip (for Body ear thing ) | Rmt | 300
9 | POWER CABLES :
Supply, laying, testing and commissioning of following size 1.1KV Grade Aluminum XLPE / Copper Conductor XLPE insulated PVC Sheathed Armoured under ground cable and shall be laid in built up cable trench/ already laid RCC Hume pipe or on cable tray (indoor/outdoor). with all installation materials as required. The cable shall conform to IS 1554/ Part I.For buried cables, the excavation work will be included under the heading "Civil works for outdoor cable laying." ( MAKES: UNIVERSAL / CCI Tropodur / NICCO / KEI )
9.01 | 3 Core x 2.5 Sqmm Copper armoured Cable. | Rmt | 100
9.02 | 7 Core x 2.5 Sqmm Copper armoured Cable. | Rmt | 200
9.03 | 12 Core x 2.5 Sqmm Copper armoured Cable. | Rmt | 200
9.04 | 24 Core x 2.5 Sqmm Copper armoured Cable. | Rmt | 100
10 | CABLE END TERMINATION :
Supply and Providing Non flame proof cable end terminations with Double compression type SS Gland, Bi-metallic Heavy duty lugs , insulation tape, identification Aluminum Engraved tags etc.With including Gland Earthing, Drilling for Gland complete as required.(Make-HMI/ comet, Lugs: DOWELLS/HEX).
10.01 | 3 Core x 2.5 Sqmm Copper armoured Cable. | No | 8
10.02 | 7 Core x 2.5 Sqmm Copper armoured Cable. | No | 12
10.03 | 12 Core x 2.5 Sqmm Copper armoured Cable. | No | 8
10.04 | 24 Core x 2.5 Sqmm Copper armoured Cable. | No | 8
11 | L.T BUS DUCT
Supply, store, receive, erection, testing & commissioning of 415V, Non Segregated IP 65 LT Bus duct made out of 14 SWG CRCA Sheet after seven tank process and painting with Epoxy powder coating. Bus duct shall consist of suitable rating Three Phase + 100% N with 2 run Earth strip Externally & 50% earth internally Aluminum bus bar (at the rating of 0.8 A /Sq.mm) color coded with Heat shrinkable sleeves with continuous Earth Bus on both side of bus duct with accessories as required. . Steel item required for supporting the bus duct will be operate under Steel item heading. ( BUS DUCT Make:- L&T / Schneider )
11.01 | Supply and fixing of 2000A 415V, TP+1N+2E, Aluminum Sandwich Bus Trunking / Bus duct suitable for Indoor application. With external double ear thing. | Rmt | 20
11.02 | Supply and fixing of 2000A 415V, TPN+E 90 Deg Bend of LHS (or) RHS Vertical Suitable for indoor type application. | No | 2
11.03 | Supply and fixing of 2000A 415V, TPN+E 90 Deg Bend of LHS (or) RHS Horizontal Suitable for indoor type application. | No | 2
11.04 | 2000A , 415V, TP+1N+2E Flange end adopter box with Suitable Flange end Elbow (or) Flanged End , flange bellow ,rubber cushion suitable for indoor / out door type application for connecting the bus duct with Transformer terminals (or) DG end (or) Panel terminals with all necessary Fixing and supporting accessories etc as required. the quoted cost shall inclusive of Phase cross over as required. | No | 4
11.05 | Supply and fixing of 2000A 415V, TP+1N+2E, Aluminum Sandwich Bus Trunking / Bus duct suitable for Outdoor application. With external double ear thing. | Rmt | 10
11.06 | Supply and fixing of 2000A 415V, TPN+E 90 Deg Bend of LHS (or) RHS Vertical Suitable for Outdoor type application. | No | 2
11.07 | Supply and fixing of 2000A 415V, TPN+E 90 Deg Bend of LHS (or) RHS Horizontal Suitable for Outdoor type application. | No | 2
11.08 | Supply and Providing the 2000A TP+1N+2E laminated copper flexible bimetallic of required length ( minimum 400mm ) with necessary all fixing electrolyte grade hardware's as required. | set | 4
11.09 | Supply and fixing of 4000 A 415V, TP+1N+2E, Aluminum Sandwich Bus duct with Uni block joints suitable for indoor application With external double ear thing | RMT | 10
11.1 | Supply and fixing of 4000 A 415V, TPN+E , 90 Degree Bend (or ) Offset Edge Elbow (or ) Edge Elbow (or ) LHS (or) RHS Vertical (or ) horizontal bends Suitable for intdoor type application. | No | 4
11.11 | Supply and Providing the 4000 A TP+1N+2E laminated copper flexible ,with bimetallic end ( minimum length 300mm ) as required length with necessary all fixing electrolyte grade hardware's as required to connect Flanged End Bus bar with Transformer (or) DG (or) LT panels' terminal.. | set | 2
11.12 | 4000A , 415V, TP+1N+2E Flange end adopter box with Suitable Flange end Elbow (or) Flanged End , flange bellow ,rubber cushion suitable for indoor / out door type application for connecting the bus duct with Transformer terminals (or) DG end (or) Panel terminals with all necessary Fixing and supporting accessories etc as required. the quoted cost shall inclusive of Phase cross over as required. | set | 2
TOTAL COST
GRAND TOTAL OF SUPPLY AND ERECTIONS ====>
TOTAL VALUE OF E.D
TOTAL VALUE OF CST
TOTAL VALUE OF VAT
TOTAL VALUE OF SER. TAX
GRAND TOTAL INCLUSIVE OF ALL DUTIES & TAXES
Note :
A ) if any change in MEP services load will affect the DG as well transformers size etc.
B) all the DG sets should be continuous Duty ,prime power ratting only
C ) quoted cost should inclusive of all taxes , duty ,octroi, transport etc
EXCLUSION OF ITEMS
MASONARY CABLE TRENCH
RCC /PCC FOUNDATION For the DG sets and Panels
SMOKE EXHAUS T STRUCTURE'S CIVIL FOUNDATION
| SIGNATURE OF CLIENTS WITH SEAL |  |  |  |  | SIGNATURE OF BIDDER WITH SEAL
Note on E20: RAMESH: As per client mail on 03.12.15 we removed MSME shead DG pack up
Note on E99: RAMESH: As per client mail on 03.12.15 we removed MSME shead DG pack up